## Instructions
Instructions | Version:
Fill out Customer and Contractor/Vendor Information fields at the top. | 2022-04-06
For each new measure installed, enter the relevant information from left to right. Be sure to enter the Building Type first.
Measures are specified by measure code with a pulldown. "HVAC Measure List" sheet has the details on the measure iterations for each measure code that can be selected in Column D of the "Electric HVAC" sheet.
Columns J:AD of the "Electric HVAC" sheet have measure-specific entries. Measure-specific fields that are required for entry and are related to each measure's qualification requirements are in light blue within a row depending on the measure code chosen in Column D. Fields that are unnecessary for calculating measure impacts or qualification are greyed out within the respective row. Entries which do not meet efficiency or capacity requirements are highlighted in light red within a row .
The Installed Cost of Line Item column must be filled out; otherwise the incentives will not populate. For this field, please enter the cost of labor and materials before sales tax for each individual line item.
The New Unit Quantity in Column P is required for HVAC Equipment measures; Number of Units (Number of Individual Controls) in Column P is required for Other/HVAC Controls measures. These must be populated according to measure in question in order for an incentive to be calculated.
Please do not insert line breaks within input cells; this can break the tracking system import functionality of this calculator.

## Electric HVAC
|  | Customer Information: |  |  |  | Contractor/Vendor Information:
|  | PREMISE NAME: |  |  |  | COMPANY NAME:
PROJECT NUMBER
|  | ACCOUNT NUMBER: |  |  |  | Project Summary
|  | TOTAL MATERIAL COST: |  |  |  | Estimated Project Incentive | 0
|  | TOTAL LABOR COST: |  |  |  | Estimated Project Savings (kWh/yr) | 0
|  | TOTAL PROJECT COST: |  |  |  | Estimated Project Savings (kW) | 0
| Facility Information |  | Measure Information - HVAC Equipment | [15 empty] | Measure Information - HVAC Controls | [10 empty] | Incentive Information |  |  | Savings | Error Message
| Facility Type | Building Type | Measure Code [Required Entry] (See "HVAC Measure Inputs" tab) | Unit Type | AC or Heat Pump | Efficiency Requirements | Minimum Capacity (Btu/h) | Maximum Capacity (Btu/h) | New Unit Cooling Capacity (Btuh) [Required] | New Unit SEER / IEER Part-Load Efficiency [Required] | New Unit EER Full Load Efficiency [Required] | New Unit Heating Capacity (Btuh) [Required if Heat Pump] | New Unit Heating Efficiency [Required if Heat Pump] | Heating Efficiency Type | New Unit Quantity [Required] | Manufacturer [Required] | Model [Required] | Serial Number | Number of Units (Other HVAC/Controls) | Is Controlled Equipment New or Existing? | Type of Equipment Controlled | Cooling Capacity of Controlled Equipment (Btu/h) - Per Control - | Cooling Efficiency EER (or SEER below 65,000 Btu/h) | Heating Capacity of Controlled Equipment (Btu/h) - Per Control - | Heating Efficiency COP or HSPF - Electric Only - | Heating Efficiency Metric (COP or HSPF) | Baseline Thermostat Type | Cooling Season Facility Temp (°F) | Heating Season Facility Temp (°F) | Installed Cost of Line Item [Required] | Incentive per Ton/Unit | Estimated Line Item Incentive | Estimated Savings (kWh per Year)
[10 empty] | Except for Equipment without SEER/IEER Rating |  | Required for all Heat Pumps | HSPF for ASHP under 65 kBtu/h and ductless, COP for all other |  |  | Required for All Measures - Replacement and Control | Required for All Measures - Replacement and Control |  | All HVAC Controls | All HVAC Controls | All HVAC Controls | All HVAC Controls | For Thermostat and Hotel Room Controls Only | For Thermostat and Hotel Room Controls Only | For Thermostat and Hotel Room Controls Only |  | For Smart Thermostats only | For Hotel Room Controls Only | For Hotel Room Controls Only
1 | Commercial_Industrial
2 | Commercial_Industrial
3 | Commercial_Industrial
4 | Commercial_Industrial
5 | Commercial_Industrial
6 | Commercial_Industrial
7 | Commercial_Industrial
8 | Commercial_Industrial
9 | Commercial_Industrial
10 | Commercial_Industrial
11 | Commercial_Industrial
12 | Commercial_Industrial
13 | Commercial_Industrial
14 | Commercial_Industrial
15 | Commercial_Industrial
16 | Commercial_Industrial
17 | Commercial_Industrial
18 | Commercial_Industrial
19 | Commercial_Industrial
20 | Commercial_Industrial
21 | Commercial_Industrial
22 | Commercial_Industrial
23 | Commercial_Industrial
24 | Commercial_Industrial
25 | Commercial_Industrial
26 | Commercial_Industrial
27 | Commercial_Industrial
28 | Commercial_Industrial
29 | Commercial_Industrial
30 | Commercial_Industrial
31 | Commercial_Industrial
32 | Commercial_Industrial
Note on X10: Efficiencies autofilled with relevant ASHRAE 90.1 standards (based on new/existing vintage) if left blank. Do not leave blank for "Other" system
Note on Z10: Efficiencies autofilled with relevant ASHRAE 90.1 standards (based on new/existing vintage) if left blank. Do not leave blank for "Other" system
Note on AE10: Please enter the pre-tax cost equipment and labor measure on each individual line

## Unit Savings (hidden)
[37 empty] | FALSE | [30 empty] | Error Messages
[27 empty] | #N/A | [9 empty] | Dual Enthalpy Economizer Controls | Thermostat - Smart | Thermostat - Smart | Hotel Room HVAC Controls | Hotel Room HVAC Controls | [18 empty] | For conditioning formatting
| Application Inputs - HVAC Equipment | [11 empty] | Application Inputs - Other HVAC | [6 empty] | Measure Inputs |  |  |  |  | Savings Inputs - HVAC Equipment | [9 empty] | Savings Inputs - Other HVAC | [6 empty] | Measure Savings |  |  |  | Lifetime Savings |  |  |  | Incentive Information |  | Vision-Specific Data | [7 empty] | SEER/IEER_q | New Unit EER | COP_q
| Facility Type | Building Type | Measure Code | Measure Type | AC/HP | Number of Units | Cooling Capacity (Btu/h) | New Unit SEER / IEER | New Unit EER | New Unit Heating Capacity (Btuh) [Required if Heat Pump] | New Unit Heating Efficiency COP Btu/Btu HSPF ALREADY DIVIDED BY 3.412 | Heating Efficiency Type (original) | Number of Units | Cooling Capacity (kBtu/h) | Cooling Efficiency EER (or SEER below 65,000 Btu/h) | Heating Capacity of Controlled Equipment (kBtu/h) | Heating Efficiency Btu/Wh COP ALREADY MULTIPLIED BY 3.412 | Heating Season Facility Temp (°F) | Cooling Season Facility Temp (°F) | Baseline SEER/ IEER | Baseline EER | Baseline COP | Baseline HSPF | Measure Life | SEER/IEER_b | SEER/IEER_q | IEER/SEER Base for NJCEP Energy Calc | IEER/SEER Qual for NJCEP Energy Calc | EER (or SEER) Base for KW Calc | EER (or SEER) Eff for KW Calc | COP_b | COP_q | EFLH_h | EFLH_c | Heating Season Setback Temp (°F) | Cooling Season Setback Temp (°F) | Economizer Savings kWh | Thermostat Savings - Cooling kWh | Thermostat Savings - Heating kWh | HVAC Occ Ctrl Savings - Cooling KWh | HVAC Occ Ctrl Savings - Heating kWh | Cooling Energy Savings [kWh/yr] | Heating Energy Savings [kWh/yr] | Energy Savings [kWh/yr] | Peak Demand Savings [kW] | Cooling Energy Savings [kWh] | Heating Energy Savings [kWh] | Energy Savings [kWh] | Peak Demand Savings [kW] | Incentive per Ton/Unit | Total Incentive | Gas Utility Incentive | Total Incentive (Gas + Electric) | Annual MMBtu Savings (Gas + Electric) | Lifetime MMBtu Savings (Gas + Electric) | Imports Qual |  |  |  | Checks Qual |  |  | Zeroes out incentive | For conditional formatting
[56 empty] | Min Qualifying SEER/IEER | Min Qualifying EER | Min Qualifying HSPF | Min Qualifying COP | Min Qualifying SEER/IEER | Min Qualifying EER | Min Qualifying COP | Unit Qualifies? | Does not meet SEER/IEER | Does not meet EER | Does not meet COP | Heat Pump? | Please check that equipment efficiencies meet qualification requirements. | Please enter installed cost of line item. | Please enter manufacturer and model information. | Please check that the equipment capacity matches the measure code requirements. | Savings Multiplier
1 | Commercial_Industrial | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [6 empty] | 0 | [5 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A |  |  |  | Yes | FALSE | FALSE | FALSE | TRUE | 1 | 1 | 1 | 1 | 1
2 | Commercial_Industrial | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [6 empty] | 0 | [5 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A |  |  |  | Yes | FALSE | FALSE | FALSE | TRUE | 1 | 1 | 1 | 1 | 1
3 | Commercial_Industrial | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [6 empty] | 0 | [5 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A |  |  |  | Yes | FALSE | FALSE | FALSE | TRUE | 1 | 1 | 1 | 1 | 1
4 | Commercial_Industrial | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [6 empty] | 0 | [5 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A |  |  |  | Yes | FALSE | FALSE | FALSE | TRUE | 1 | 1 | 1 | 1 | 1
5 | Commercial_Industrial | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [6 empty] | 0 | [5 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A |  |  |  | Yes | FALSE | FALSE | FALSE | TRUE | 1 | 1 | 1 | 1 | 1
6 | Commercial_Industrial | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [6 empty] | 0 | [5 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A |  |  |  | Yes | FALSE | FALSE | FALSE | TRUE | 1 | 1 | 1 | 1 | 1
7 | Commercial_Industrial | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [6 empty] | 0 | [5 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A |  |  |  | Yes | FALSE | FALSE | FALSE | TRUE | 1 | 1 | 1 | 1 | 1
8 | Commercial_Industrial | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [6 empty] | 0 | [5 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A |  |  |  | Yes | FALSE | FALSE | FALSE | TRUE | 1 | 1 | 1 | 1 | 1
9 | Commercial_Industrial | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [6 empty] | 0 | [5 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A |  |  |  | Yes | FALSE | FALSE | FALSE | TRUE | 1 | 1 | 1 | 1 | 1
10 | Commercial_Industrial | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [6 empty] | 0 | [5 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A |  |  |  | Yes | FALSE | FALSE | FALSE | TRUE | 1 | 1 | 1 | 1 | 1
11 | Commercial_Industrial | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [6 empty] | 0 | [5 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A |  |  |  | Yes | FALSE | FALSE | FALSE | TRUE | 1 | 1 | 1 | 1 | 1
12 | Commercial_Industrial | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [6 empty] | 0 | [5 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A |  |  |  | Yes | FALSE | FALSE | FALSE | TRUE | 1 | 1 | 1 | 1 | 1
13 | Commercial_Industrial | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [6 empty] | 0 | [5 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A |  |  |  | Yes | FALSE | FALSE | FALSE | TRUE | 1 | 1 | 1 | 1 | 1
14 | Commercial_Industrial | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [6 empty] | 0 | [5 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A |  |  |  | Yes | FALSE | FALSE | FALSE | TRUE | 1 | 1 | 1 | 1 | 1
15 | Commercial_Industrial | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [6 empty] | 0 | [5 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A |  |  |  | Yes | FALSE | FALSE | FALSE | TRUE | 1 | 1 | 1 | 1 | 1
16 | Commercial_Industrial | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [6 empty] | 0 | [5 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A |  |  |  | Yes | FALSE | FALSE | FALSE | TRUE | 1 | 1 | 1 | 1 | 1
17 | Commercial_Industrial | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [6 empty] | 0 | [5 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A |  |  |  | Yes | FALSE | FALSE | FALSE | TRUE | 1 | 1 | 1 | 1 | 1
18 | Commercial_Industrial | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [6 empty] | 0 | [5 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A |  |  |  | Yes | FALSE | FALSE | FALSE | TRUE | 1 | 1 | 1 | 1 | 1
19 | Commercial_Industrial | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [6 empty] | 0 | [5 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A |  |  |  | Yes | FALSE | FALSE | FALSE | TRUE | 1 | 1 | 1 | 1 | 1
20 | Commercial_Industrial | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [6 empty] | 0 | [5 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A |  |  |  | Yes | FALSE | FALSE | FALSE | TRUE | 1 | 1 | 1 | 1 | 1
21 | Commercial_Industrial | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [6 empty] | 0 | [5 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A |  |  |  | Yes | FALSE | FALSE | FALSE | TRUE | 1 | 1 | 1 | 1 | 1
22 | Commercial_Industrial | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [6 empty] | 0 | [5 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A |  |  |  | Yes | FALSE | FALSE | FALSE | TRUE | 1 | 1 | 1 | 1 | 1
23 | Commercial_Industrial | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [6 empty] | 0 | [5 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A |  |  |  | Yes | FALSE | FALSE | FALSE | TRUE | 1 | 1 | 1 | 1 | 1
24 | Commercial_Industrial | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [6 empty] | 0 | [5 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A |  |  |  | Yes | FALSE | FALSE | FALSE | TRUE | 1 | 1 | 1 | 1 | 1
25 | Commercial_Industrial | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [6 empty] | 0 | [5 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A |  |  |  | Yes | FALSE | FALSE | FALSE | TRUE | 1 | 1 | 1 | 1 | 1
26 | Commercial_Industrial | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [6 empty] | 0 | [5 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A |  |  |  | Yes | FALSE | FALSE | FALSE | TRUE | 1 | 1 | 1 | 1 | 1
27 | Commercial_Industrial | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [6 empty] | 0 | [5 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A |  |  |  | Yes | FALSE | FALSE | FALSE | TRUE | 1 | 1 | 1 | 1 | 1
28 | Commercial_Industrial | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [6 empty] | 0 | [5 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A |  |  |  | Yes | FALSE | FALSE | FALSE | TRUE | 1 | 1 | 1 | 1 | 1
29 | Commercial_Industrial | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [6 empty] | 0 | [5 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A |  |  |  | Yes | FALSE | FALSE | FALSE | TRUE | 1 | 1 | 1 | 1 | 1
30 | Commercial_Industrial | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [6 empty] | 0 | [5 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A |  |  |  | Yes | FALSE | FALSE | FALSE | TRUE | 1 | 1 | 1 | 1 | 1
31 | Commercial_Industrial | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [6 empty] | 0 | [5 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A |  |  |  | Yes | FALSE | FALSE | FALSE | TRUE | 1 | 1 | 1 | 1 | 1
32 | Commercial_Industrial | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [6 empty] | 0 | [5 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A |  |  |  | Yes | FALSE | FALSE | FALSE | TRUE | 1 | 1 | 1 | 1 | 1
NAME | Electric Unitary HVAC - 2021 | Electric Unitary HVAC - 2021 | Electric Unitary HVAC - 2021 | Electric Unitary HVAC - 2021 | Electric Unitary HVAC - 2021 | Electric Unitary HVAC - 2021 | Electric Unitary HVAC - 2021 | Electric Unitary HVAC - 2021 | Electric Unitary HVAC - 2021 |  | Electric Unitary HVAC - 2021 | Electric Unitary HVAC - 2021 | Electric Unitary HVAC - 2021 | Electric Unitary HVAC - 2021 |  |  |  | Electric Unitary HVAC - 2021 | Electric Unitary HVAC - 2021 | Electric Unitary HVAC - 2021 | Electric Unitary HVAC - 2021 | Electric Unitary HVAC - 2021 | Electric Unitary HVAC - 2021 | Electric Unitary HVAC - 2021 | Electric Unitary HVAC - 2021 | Electric Unitary HVAC - 2021 |  |  | Electric Unitary HVAC - 2021 | Electric Unitary HVAC - 2021 | Electric Unitary HVAC - 2021 | Electric Unitary HVAC - 2021 | Electric Unitary HVAC - 2021 | Electric Unitary HVAC - 2021 | Electric Unitary HVAC - 2021 | Electric Unitary HVAC - 2021 | [5 empty] | Electric Unitary HVAC - 2021 | Electric Unitary HVAC - 2021 | Electric Unitary HVAC - 2021 | Electric Unitary HVAC - 2021 | Electric Unitary HVAC - 2021 | Electric Unitary HVAC - 2021 | Electric Unitary HVAC - 2021 | Electric Unitary HVAC - 2021 | Electric Unitary HVAC - 2021 | Electric Unitary HVAC - 2021 | Electric Unitary HVAC - 2021 | Electric Unitary HVAC - 2021 | Electric Unitary HVAC - 2021 | Electric Unitary HVAC - 2021
ATTRNAME | facility_type | building_type | MEASURE_CODE | Description | cooling_type | Number_Units | Capacity |  |  | capacity_heating |  |  | number_units_recommended | Tons | Efficiency | Tons_Controlled |  | Temp_Heat | Temp_Cool |  |  |  | Baseline_HSPF | MEASURE_LIFE |  |  | basecase_seer | SEER | Baseline_EER | EER | Baseline_COP | COP | Full_Load_Hours_Heat | Full_Load_Hours_Cool | set_back_temp_heat | set_back_temp_cooling | [5 empty] | KWH_Cooling | kWh_heating | KWH_IMPACT | KW_IMPACT |  |  | LIFETIME_SAVINGS | kw_impact_1 | incentive_rate | ELEC_UTIL_CUST_INCENTIVE | GAS_UTIL_CUST_INCENTIVE | INCENTIVE_AMOUNT | NATURAL_GAS_SAVINGS_MMBTU | Total_MMBTU
DEFAULTVALUE | [51 empty] | 0
ITEMORDER | 1 | 2 | 3 | 4 | 5 | 6 | 7 | [5 empty] | 1 | 2 | 6 | 5 |  | 3 | 4 |  |  |  | 7 | 8 |  |  | 1 | 2 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | [5 empty] | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22
FRIENDLYNAME | Facility Type | Building Type | Measure Code | Measure Type | AC/HP | Number of Units | Cooling Capacity (Btu/h) |  |  | Heating Capacity (Btu/h) |  |  | Number of Units - Other HVAC | Cooling Capacity of Controlled Equipment (kBtu/h) | Controlled Cooling Efficiency EER/SEER | Heating Capacity of Controlled Equipment (kBtu/h) |  | Heating Season Facility Temp (*F) - Other HVAC | Cooling Season Facility Temp (*F) - Other HVAC |  |  |  | Baseline HSPF | Measure Life |  |  | Baseline SEER/EER for kWh | Efficient SEER/EER for kWh | Baseline EER for kW | Efficient EER for kW | Baseline COP | Efficient COP | EFLH_h | EFLH_c | Heating Season Setback Temp (*F) | Cooling Season Setback Temp (*F) | [5 empty] | Cooling Energy Savings [kWh/yr] | Heating Energy Savings [kWh/yr] | Gross Annual Electric Savings (kWh) | Gross Annual Electric Peak Demand Reduction (kW) |  |  | Gross Lifetime Electric Savings (kWh) | Lifetime Peak Demand Savings [kW] | Incentive per Ton/Unit | Electric Utility Incentive | Gas Utility Incentive | Total Incentive | Annual MMBtu Savings (Gas + Electric) | Lifetime MMBtu Savings (Gas + Electric)
TOOLTIP
DATADESC
VALIDATIONTYPE | text | text | text | text | text | numeric | numeric |  |  | numeric |  |  | numeric | numeric | numeric | numeric |  | numeric | numeric |  |  |  | numeric | numeric |  |  | numeric | numeric | numeric | numeric | numeric | numeric | numeric | numeric | numeric | numeric | [5 empty] | numeric | numeric | numeric | numeric |  |  | numeric | numeric | numeric | numeric | numeric | numeric | numeric | numeric
VALIDATIONOTHER
VALIDATIONREQ | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE |  |  | FALSE |  |  | FALSE | FALSE | FALSE | FALSE |  | FALSE | FALSE |  |  |  | FALSE | FALSE |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | [5 empty] | FALSE | FALSE | FALSE | FALSE |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
LOWLIMIT
HIGHLIMIT
SHOWALL | N | N | N | N | N | N | N |  |  | Y |  |  | N | N | N | N |  | N | N |  |  |  | N | N |  |  | N | N | N | N | N | N | N | N | N | N | bar: 9 to 12; 15 to 0 22
EDITALL | N | N | N | N | N | N | N |  |  | Y |  |  | N | N | N | N |  | N | N |  |  |  | N | N |  |  | N | N | N | N | N | N | N | N | N | N | bar: 9 to 12; 15 to 0 22
LOOKUPVALUES
**** Changed to use EER for energy savings calculations per NJCEP protocols, contrary to recommendations of the Uniform Methods Project.

## HVAC Measure List
Measure Code | Type Abbreviation | AC or Heat Pump | Unit Type | Capacity | Tier | Efficiency Requirements | Minimum Capacity (Btuh) | Maximum Capacity (Btuh) | Baseline SEER/ IEER | Baseline EER | Baseline COP | Baseline HSPF | Min Qualifying SEER/IEER | Min Qualifying EER | Min Qualifying HSPF | Min Qualifying COP | Incentive per Ton/Unit | Measure Life | AEG Measure | EM&V Measure | Heating Rating Type | Cooling Rating Type for Savings | Column for kWh Match | kW Calculation based on: | Column for kW Match
H1 - CV7001 | S | AC | Split System - S - Tier 1 | < 5.4 tons | 1 | 16 SEER | 1 | 64999 | 13 | N/A | N/A | N/A | 16 | 0 | N/A | N/A | 75 | 15 | H1 | CV7001 |  | SEER | 1 | SEER | 1
H2 - CV7002 | S | AC | Split System - S - Tier 2 | < 5.4 tons | 2 | 18 SEER | 1 | 64999 | 13 | N/A | N/A | N/A | 18 | 0 | N/A | N/A | 100 | 15 | H2 | CV7002 |  | SEER | 1 | SEER | 1
H3 - CV7001 | P | AC | Single Package - P - Tier 1 | < 5.4 tons | 1 | 16 SEER | 1 | 64999 | 13 | N/A | N/A | N/A | 16 | 0 | N/A | N/A | 75 | 15 | H3 | CV7001 |  | SEER | 1 | SEER | 1
H4 - CV7002 | P | AC | Single Package - P - Tier 2 | < 5.4 tons | 2 | 18 SEER | 1 | 64999 | 13 | N/A | N/A | N/A | 18 | 0 | N/A | N/A | 100 | 15 | H4 | CV7002 |  | SEER | 1 | SEER | 1
H5 - CV7005 | S/P | AC | Split System - S or Single Package - P - Tier 1 | >= 5.4 to <11.25 tons | 1 | 13.3 IEER / 11.6 EER | 65000 | 134999 | 12.7 | 11 | N/A | N/A | 13.3 | 11.6 | N/A | N/A | 80 | 15 | H5 | CV7005 |  | IEER | 1 | EER | 2
H6 - CV7005 | S/P | AC | Split System - S or Single Package - P - Tier 2 | >= 5.4 to <11.25 tons | 2 | 14.0 IEER / 12.5 EER | 65000 | 134999 | 12.7 | 11 | N/A | N/A | 14 | 12.5 | N/A | N/A | 80 | 15 | H6 | CV7005 |  | IEER | 1 | EER | 2
H7 - CV7005 | S/P | AC | Split System - S or Single Package - P - Tier 1 | >= 11.25 to < 20 tons | 1 | 12.8 IEER / 11.3 EER | 135000 | 239999 | 12.2 | 10.8 | N/A | N/A | 12.8 | 11.3 | N/A | N/A | 80 | 15 | H7 | CV7005 |  | IEER | 1 | EER | 2
H8 - CV7005 | S/P | AC | Split System - S or Single Package - P - Tier 2 | >= 11.25 to < 20 tons | 2 | 14.0 IEER / 12.0 EER | 135000 | 239999 | 12.2 | 10.8 | N/A | N/A | 14 | 12 | N/A | N/A | 80 | 15 | H8 | CV7005 |  | IEER | 1 | EER | 2
H9 - CV7005 | D | AC | Central DX AC - D - Tier 1 | >= 20 to < 63 tons | 1 | 12.0 IEER / 10.3 EER | 240000 | 759999 | 11.4 | 9.8 | N/A | N/A | 12 | 10.3 | N/A | N/A | 80 | 15 | H9 | CV7005 |  | IEER | 1 | EER | 2
H10 - CV7005 | D | AC | Central DX AC - D - Tier 2 | >= 20 to < 63 tons | 2 | 12.5 IEER / 11.0 EER | 240000 | 759999 | 11.4 | 9.8 | N/A | N/A | 12.5 | 11 | N/A | N/A | 80 | 15 | H10 | CV7005 |  | IEER | 1 | EER | 2
H11 - CV7005 | D | AC | Central DX AC - D - Tier 1 | > 63 tons | 1 | 11.6 IEER / 10.0 EER | 760000 | 999999999 | 11 | 9.5 | N/A | N/A | 11.6 | 10 | N/A | N/A | 80 | 15 | H11 | CV7005 |  | IEER | 1 | EER | 2
H12 - CV7005 | D | AC | Central DX AC - D - Tier 2 | > 63 tons | 2 | 12.0 IEER / 10.0 EER | 760000 | 999999999 | 11 | 9.5 | N/A | N/A | 12 | 10 | N/A | N/A | 80 | 15 | H12 | CV7005 |  | IEER | 1 | EER | 2
H13 - CV7003 | AS | HP | Air Source Heat Pump (Split System) - AS - Tier 1 | < 5.4 tons | 1 | 16 SEER / 13 EER / 10 HSPF | 1 | 64999 | 14 | N/A | N/A | 8.2 | 16 | 13 | 10 | 2.9308 | 75 | 15 | H13 | CV7003 | HSPF | SEER | 1 | SEER | 1
H14 - CV7004 | AS | HP | Air Source Heat Pump (Split System) - AS - Tier 2 | < 5.4 tons | 2 | 18 SEER / 13 EER / 10 HSPF | 1 | 64999 | 14 | N/A | N/A | 8.2 | 18 | 13 | 10 | 2.9308 | 100 | 15 | H14 | CV7004 | HSPF | SEER | 1 | SEER | 1
H15 - CV7003 | AP | HP | Air Source Heat Pump (Single Package) - AP - Tier 1 | < 5.4 tons | 1 | 16 SEER / 13 EER / 10 HSPF | 1 | 64999 | 14 | N/A | N/A | 8 | 16 | 13 | 10 | 2.9308 | 75 | 15 | H15 | CV7003 | HSPF | SEER | 1 | SEER | 1
H16 - CV7004 | AP | HP | Air Source Heat Pump (Single Package) - AP - Tier 2 | < 5.4 tons | 2 | 18 SEER / 13 EER / 10 HSPF | 1 | 64999 | 14 | N/A | N/A | 8 | 18 | 13 | 10 | 2.9308 | 100 | 15 | H16 | CV7004 | HSPF | SEER | 1 | SEER | 1
H17 - CV7006 | AS | HP | Air Source Heat Pump (Split System) - AS - Tier 1 | >= 5.4 to <11.25 tons | 1 | 12.6 IEER / 11.3 EER / 3.5 COP | 65000 | 134999 | 11 | 10.8 | 3.3 | 12.6 | 12.6 | 11.3 | N/A | 3.5 | 80 | 15 | H17 | CV7006 | COP | IEER | 1 | EER | 2
H18 - CV7006 | AS | HP | Air Source Heat Pump (Split System) - AS - Tier 2 | >= 5.4 to <11.25 tons | 2 | 12.8 IEER / 12.1 EER / 3.5 COP | 65000 | 134999 | 11 | 10.8 | 3.3 | N/A | 12.8 | 12.1 | N/A | 3.5 | 80 | 15 | H18 | CV7006 | COP | IEER | 1 | EER | 2
H19 - CV7006 | AS | HP | Air Source Heat Pump (Split System) - AS - Tier 1 | >= 11.25 to < 20 tons | 1 | 11.9 IEER / 10.9 EER / 3.4 COP | 135000 | 239999 | 11.4 | 10.4 | 3.2 | N/A | 11.9 | 10.9 | N/A | 3.4 | 80 | 15 | H19 | CV7006 | COP | IEER | 1 | EER | 2
H20 - CV7006 | AS | HP | Air Source Heat Pump (Split System) - AS - Tier 2 | >= 11.25 to < 20 tons | 2 | 15.0 IEER / 11.7 EER / 3.3 COP | 135000 | 239999 | 11.4 | 10.4 | 3.2 | N/A | 15 | 11.7 | N/A | 3.3 | 80 | 15 | H20 | CV7006 | COP | IEER | 1 | EER | 2
H21 - CV7006 | AS | HP | Air Source Heat Pump (Split System) - AS - Tier 1 | >= 20 tons | 1 | 10.9 IEER / 9.8 EER / 3.4 COP | 240000 | 999999999 | 10.4 | 9.3 | 3.2 | N/A | 10.9 | 9.8 | N/A | 3.4 | 80 | 15 | H21 | CV7006 | COP | IEER | 1 | EER | 2
H22 - CV7006 | AS | HP | Air Source Heat Pump (Split System) - AS - Tier 2 | >= 20 tons | 2 | 12.0 IEER / 9.7 EER / 3.2 COP | 240000 | 999999999 | 10.4 | 9.3 | 3.2 | N/A | 12 | 9.7 | N/A | 3.2 | 80 | 15 | H22 | CV7006 | COP | IEER | 1 | EER | 2
H23 - CV7006 | AP | HP | Air Source Heat Pump (Single Package) - AP - Tier 1 | >= 5.4 to <11.25 tons | 1 | 12.6 IEER / 11.3 EER / 3.5 COP | 65000 | 134999 | 12 | 10.8 | 3.3 | N/A | 12.6 | 11.3 | N/A | 3.5 | 80 | 15 | H23 | CV7006 | COP | IEER | 1 | EER | 2
H24 - CV7006 | AP | HP | Air Source Heat Pump (Single Package) - AP - Tier 2 | >= 5.4 to <11.25 tons | 2 | 12.8 IEER / 12.1 EER / 3.5 COP | 65000 | 134999 | 12 | 10.8 | 3.3 | N/A | 12.8 | 12.1 | N/A | 3.5 | 80 | 15 | H24 | CV7006 | COP | IEER | 1 | EER | 2
H25 - CV7006 | AP | HP | Air Source Heat Pump (Single Package) - AP - Tier 1 | >= 11.25 to < 20 tons | 1 | 11.9 IEER / 10.9 EER / 3.4 COP | 135000 | 239999 | 11.4 | 10.4 | 3.2 | N/A | 11.9 | 10.9 | N/A | 3.4 | 80 | 15 | H25 | CV7006 | COP | IEER | 1 | EER | 2
H26 - CV7006 | AP | HP | Air Source Heat Pump (Single Package) - AP - Tier 2 | >= 11.25 to < 20 tons | 2 | 15.0 IEER / 11.7 EER / 3.3 COP | 135000 | 239999 | 11.4 | 10.4 | 3.2 | N/A | 15 | 11.7 | N/A | 3.3 | 80 | 15 | H26 | CV7006 | COP | IEER | 1 | EER | 2
H27 - CV7006 | AP | HP | Air Source Heat Pump (Single Package) - AP - Tier 1 | >= 20 tons | 1 | 10.9 IEER / 9.8 EER / 3.4 COP | 240000 | 999999999 | 10.4 | 9.3 | 3.2 | N/A | 10.9 | 9.8 | N/A | 3.4 | 80 | 15 | H27 | CV7006 | COP | IEER | 1 | EER | 2
H28 - CV7006 | AP | HP | Air Source Heat Pump (Single Package) - AP - Tier 2 | >= 20 tons | 2 | 12.0 IEER / 9.7 EER / 3.2 COP | 240000 | 999999999 | 10.4 | 9.3 | 3.2 | N/A | 12 | 9.7 | N/A | 3.2 | 80 | 15 | H28 | CV7006 | COP | IEER | 1 | EER | 2
H29 - CV7010 | W | HP | Water Source Heat Pump - W - Tier 1 | < 1.4 tons | 1 | 12.8 EER / 4.5 COP | 1 | 16999 | N/A | 12.2 | 4.3 | N/A | N/A | 12.8 | N/A | 4.5 | 50 | 15 | H29 | CV7010 | COP | EER | 2 | EER | 2
H30 - CV7010 | W | HP | Water Source Heat Pump - W - Tier 2 | < 1.4 tons | 2 | 13.7 EER / 4.8 COP | 1 | 16999 | N/A | 12.2 | 4.3 | N/A | N/A | 13.7 | N/A | 4.8 | 100 | 15 | H30 | CV7010 | COP | EER | 2 | EER | 2
H31 - CV7010 | W | HP | Water Source Heat Pump - W - Tier 1 | >= 1.4 to < 5.4 tons | 1 | 13.7 EER / 4.5 COP | 17000 | 64999 | N/A | 13 | 4.3 | N/A | N/A | 13.7 | N/A | 4.5 | 50 | 15 | H31 | CV7010 | COP | EER | 2 | EER | 2
H32 - CV7010 | W | HP | Water Source Heat Pump - W - Tier 2 | >= 1.4 to < 5.4 tons | 2 | 14.6 EER / 4.8 COP | 17000 | 64999 | N/A | 13 | 4.3 | N/A | N/A | 14.6 | N/A | 4.8 | 100 | 15 | H32 | CV7010 | COP | EER | 2 | EER | 2
H33 - CV7010 | W | HP | Water Source Heat Pump - W - Tier 1 | >= 5.4 to <11.25 tons | 1 | 13.7 EER / 4.5 COP | 65000 | 134999 | N/A | 13 | 4.3 | N/A | N/A | 13.7 | N/A | 4.5 | 50 | 15 | H33 | CV7010 | COP | EER | 2 | EER | 2
H34 - CV7010 | W | HP | Water Source Heat Pump - W - Tier 2 | >= 5.4 to <11.25 tons | 2 | 14.6 EER / 4.8 COP | 65000 | 134999 | N/A | 13 | 4.3 | N/A | N/A | 14.6 | N/A | 4.8 | 100 | 15 | H34 | CV7010 | COP | EER | 2 | EER | 2
H35 - CV7012 | PTAC | AC | Packaged Terminal AC - PTAC |  | 1 | Calculated | 1 | 24000 | N/A | Calc | N/A | N/A | N/A | 9.975 | N/A | N/A | 100 | 15 | H35 | CV7012 |  | EER | 2 | EER | 2
H36 - CV7012 | PTHP | HP | Packaged Terminal HP - PTHP |  | 1 | Calculated | 1 | 24000 | N/A | Calc | Calc | N/A | N/A | 12.81 | N/A | 3.456 | 100 | 15 | H36 | CV7012 | COP | EER | 2 | EER | 2
H37 - CV7007 | PVAC | AC | Single Packaged Vertical AC - PVAC - Tier 1 | < 5.4 tons | 1 | 10.5 EER | 1 | 64999 | N/A | 10 | N/A | N/A | N/A | 10.5 | N/A | N/A | 75 | 15 | H37 | CV7007 |  | EER | 2 | EER | 2
H38 - CV7007 | PVAC | AC | Single Packaged Vertical AC - PVAC - Tier 2 | < 5.4 tons | 2 | 10.7 EER | 1 | 64999 | N/A | 10 | N/A | N/A | N/A | 10.7 | N/A | N/A | 100 | 15 | H38 | CV7007 |  | EER | 2 | EER | 2
H39 - CV7007 | PVAC | AC | Single Packaged Vertical AC - PVAC - Tier 1 | >= 5.4 to <11.25 tons | 1 | 10.5 EER | 65000 | 134999 | N/A | 10 | N/A | N/A | N/A | 10.5 | N/A | N/A | 45 | 15 | H39 | CV7007 |  | EER | 2 | EER | 2
H40 - CV7007 | PVAC | AC | Single Packaged Vertical AC - PVAC - Tier 2 | >= 5.4 to <11.25 tons | 2 | 10.7 EER | 65000 | 134999 | N/A | 10 | N/A | N/A | N/A | 10.7 | N/A | N/A | 45 | 15 | H40 | CV7007 |  | EER | 2 | EER | 2
H41 - CV7007 | PVAC | AC | Single Packaged Vertical AC - PVAC - Tier 1 | >= 11.25 to < 20 tons | 1 | 10.5 EER | 135000 | 239999 | N/A | 10 | N/A | N/A | N/A | 10.5 | N/A | N/A | 45 | 15 | H41 | CV7007 |  | EER | 2 | EER | 2
H42 - CV7007 | PVAC | AC | Single Packaged Vertical AC - PVAC - Tier 2 | >= 11.25 to < 20 tons | 2 | 10.7 EER | 135000 | 239999 | N/A | 10 | N/A | N/A | N/A | 10.7 | N/A | N/A | 45 | 15 | H42 | CV7007 |  | EER | 2 | EER | 2
H43 - CV7008 | PVHP | HP | Single Packaged Vertical HP - PVHP - Tier 1 | < 5.4 tons | 1 | 10.5 EER / 3.2 COP | 1 | 64999 | N/A | 10 | 3 | N/A | N/A | 10.5 | N/A | 3.2 | 45 | 15 | H43 | CV7008 | COP | EER | 2 | EER | 2
H44 - CV7008 | PVHP | HP | Single Packaged Vertical HP - PVHP - Tier 2 | < 5.4 tons | 2 | 10.7 EER / 3.2 COP | 1 | 64999 | N/A | 10 | 3 | N/A | N/A | 10.7 | N/A | 3.2 | 45 | 15 | H44 | CV7008 | COP | EER | 2 | EER | 2
H45 - CV7008 | PVHP | HP | Single Packaged Vertical HP - PVHP - Tier 1 | >= 5.4 to <11.25 tons | 1 | 10.5 EER / 3.2 COP | 65000 | 134999 | N/A | 10 | 3 | N/A | N/A | 10.5 | N/A | 3.2 | 45 | 15 | H45 | CV7008 | COP | EER | 2 | EER | 2
H46 - CV7008 | PVHP | HP | Single Packaged Vertical HP - PVHP - Tier 2 | >= 5.4 to <11.25 tons | 2 | 10.7 EER / 3.2 COP | 65000 | 134999 | N/A | 10 | 3 | N/A | N/A | 10.7 | N/A | 3.2 | 45 | 15 | H46 | CV7008 | COP | EER | 2 | EER | 2
H47 - CV7008 | PVHP | HP | Single Packaged Vertical HP - PVHP - Tier 1 | >= 11.25 to < 20 tons | 1 | 10.5 EER / 3.2 COP | 135000 | 239999 | N/A | 10 | 3 | N/A | N/A | 10.5 | N/A | 3.2 | 45 | 15 | H47 | CV7008 | COP | EER | 2 | EER | 2
H48 - CV7008 | PVHP | HP | Single Packaged Vertical HP - PVHP - Tier 2 | >= 11.25 to < 20 tons | 2 | 10.7 EER / 3.2 COP | 135000 | 239999 | N/A | 10 | 3 | N/A | N/A | 10.7 | N/A | 3.2 | 45 | 15 | H48 | CV7008 | COP | EER | 2 | EER | 2
G1 - CV7010 | WC | HP | WC - Groundwater Source Heat Pump - Tier 1 | ≤ 11.25 tons | 1 | 18.9 EER / 3.9 COP | 1 | 135000 | N/A | 18 | 3.7 | N/A | N/A | 18.9 | N/A | 3.9 | 80 | 25 | G1 | CV7010 | COP | EER | 2 | EER | 2
G2 - CV7010 | WC | HP | WC - Groundwater Source Heat Pump - Tier 2 | ≤ 11.25 tons | 2 | 20.1 EER / 4.1 COP | 1 | 135000 | N/A | 18 | 3.7 | N/A | N/A | 20.1 | N/A | 4.1 | 100 | 25 | G2 | CV7010 | COP | EER | 2 | EER | 2
G3 - CV7010 | GC | HP | GC - Ground Source Heat Pump - Tier 1 | ≤ 11.25 tons | 1 | 14.8 EER / 3.4 COP | 1 | 135000 | N/A | 14.1 | 3.2 | N/A | N/A | 14.8 | N/A | 3.4 | 80 | 25 | G3 | CV7010 | COP | EER | 2 | EER | 2
G4 - CV7010 | GC | HP | GC - Ground Source Heat Pump - Tier 2 | ≤ 11.25 tons | 2 | 15.8 EER / 3.6 COP | 1 | 135000 | N/A | 14.1 | 3.2 | N/A | N/A | 15.8 | N/A | 3.6 | 100 | 25 | G4 | CV7010 | COP | EER | 2 | EER | 2
D1 - CV7011 | DMAC | AC | Ductless Mini-Split Air Conditioner | < 7.5 tons |  | 20 SEER / 13 EER | 1 | 90000 | 13 | 11.3 | N/A | N/A | 20 | 13 | N/A | N/A | 125 | 17 | D1 | CV7011 |  | SEER | 1 | EER | 2
D2 - CV7011 | DMHP | HP | Ductless Mini-Split Heat Pump | < 7.5 tons |  | 20 SEER / 13 EER / 10 HSPF | 1 | 90000 | 14 | 12.1692 | N/A | 8.2 | 20 | 13 | 10 | 2.9308 | 125 | 17 | D2 | CV7011 | HSPF | SEER | 1 | EER | 2
O1 - CV7035 | OTH | -- | Thermostat - Smart |  |  | -- | -- | -- | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 100 | 7.5 | O1 | CV7035 |  |  | 2 |  | 2
O2 - CV7036 | OTH | -- | Dual Enthalpy Economizer Controls |  |  | -- | -- | -- | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 250 | 10 | O2 | CV7036 |  |  | 2 |  | 2
O3 - CP5002 | OTH | -- | Hotel Room HVAC Controls |  |  | -- | -- | -- | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 75 | 11 | O3 | CP5002 |  |  | 2 |  | 2
EER interpolation
Changes 2/7/2022
Changes Oct 2021

## Inspection - HVAC
| Commercial & Industrial Program | [8 empty] | Paste Inspection Pictures and Identifying Notes Here:
Inspection Form - HVAC
FOR UTILITY USE ONLY
| Inspection Type: | Post-Inspection
| Premise Name: | 0
| Account Number: | 0
| Project Number: | 0
Site Address:
| Meter Number(s) Note: 55 Character Limit per Entry |  | 55 characters left
55 characters left
55 characters left
55 characters left
Business Hours of Operation:
New Construction?
Bldg Type:
Type of AC/Heat Use:
With Gas Account?
BMS/EMS Interest?
Distributed Generation Interest?
Demand Response Interest?
| Equipment at this Facility | Equipment Description | Age of Equipment
Inspection Findings:
Other Energy Efficiency Potential:
| Inspection Review: |  | This field has to be filled out in order for inspection to upload to tracking software.
| Inspector: |  | Signature: |  | Date:
| Customer/Contractor: |  | Signature: |  | Date:
Pre-Loaded Data / Fields for Inspector Confirmation
Fields for Inspector Input
# | (pre-loaded) | (pre-loaded) | Equipment Installed, Connected, Operational? | Inspected Location | (pre-loaded) | (pre-loaded) | (pre-loaded) | (pre-loaded) | Meets Efficiency Requirements? | Temp Settings Consistent w/ Application? | Set Points Dependent on OAT? | Setback Temperatures | Customer Received O&M Manuals? | Additional Inspection Notes
| Measure Code | Measure Type (Confirm) |  |  | Manufacturer/Model (Confirm) | Serial Number | Unit Size (Btuh) (Confirm) | Verified Quantity (Confirm)
1 | 0 |  |  |  | ¦ | 0 | 0 | 0
2 | 0 |  |  |  | ¦ | 0 | 0 | 0
3 | 0 |  |  |  | ¦ | 0 | 0 | 0
4 | 0 |  |  |  | ¦ | 0 | 0 | 0
5 | 0 |  |  |  | ¦ | 0 | 0 | 0
6 | 0 |  |  |  | ¦ | 0 | 0 | 0
7 | 0 |  |  |  | ¦ | 0 | 0 | 0
8 | 0 |  |  |  | ¦ | 0 | 0 | 0
9 | 0 |  |  |  | ¦ | 0 | 0 | 0
10 | 0 |  |  |  | ¦ | 0 | 0 | 0
11 | 0 |  |  |  | ¦ | 0 | 0 | 0
12 | 0 |  |  |  | ¦ | 0 | 0 | 0
13 | 0 |  |  |  | ¦ | 0 | 0 | 0
14 | 0 |  |  |  | ¦ | 0 | 0 | 0
15 | 0 |  |  |  | ¦ | 0 | 0 | 0
16 | 0 |  |  |  | ¦ | 0 | 0 | 0
17 | 0 |  |  |  | ¦ | 0 | 0 | 0
18 | 0 |  |  |  | ¦ | 0 | 0 | 0
19 | 0 |  |  |  | ¦ | 0 | 0 | 0
20 | 0 |  |  |  | ¦ | 0 | 0 | 0
21 | 0 |  |  |  | ¦ | 0 | 0 | 0
22 | 0 |  |  |  | ¦ | 0 | 0 | 0
23 | 0 |  |  |  | ¦ | 0 | 0 | 0
24 | 0 |  |  |  | ¦ | 0 | 0 | 0
25 | 0 |  |  |  | ¦ | 0 | 0 | 0
26 | 0 |  |  |  | ¦ | 0 | 0 | 0
27 | 0 |  |  |  | ¦ | 0 | 0 | 0
28 | 0 |  |  |  | ¦ | 0 | 0 | 0
29 | 0 |  |  |  | ¦ | 0 | 0 | 0
30 | 0 |  |  |  | ¦ | 0 | 0 | 0
31 | 0 |  |  |  | ¦ | 0 | 0 | 0
32 | 0 |  |  |  | ¦ | 0 | 0 | 0
| Yes | Kevin Pfeil
| No | Jeremy Scott
Gigi Aniciete-Quijano
Patricia Moss
Mark Maloney
Jon Hilowitz
Pre-Inspection
Post-Inspection
Approved
Failed
Additional Information Needed
| Equipment Types | Equipment Age | Ice Machine Type
| Lighting - Interior | 1-2 years | Cube/Nugget
| Lighting - Exterior | 3-4 years | Flake
| HVAC | 5-6 years
| HVAC Controls | 7-8 years | Retrofit Check
| Refrigeration Equipment | 9-10 years | Adding to Existing Equipment
| Refrigeration Controls | 11-12 years | Replacing Existing Equipment
| Non-EC Motors | 13-14 years
| VFDs | 15-16 years
| Commercial Dishwasher | 17-18 years | Lighting Control Type
| Commercial Cooking Equipment | 19-20 years | Networked Lighting Controls
| Other Food Service Equipment | Unknown | Dual Daylight/Occupancy Controls
| Ice Machines |  | Daylight Controls
| Reach-in Coolers or Freezers |  | Occupancy/Vacancy Controls
Residential Appliances
| Commercial Appliances |  | Baseline Fuel Type
| Water Heaters |  | Electricity
| Plug Load Controls |  | Natural Gas
| Office Equipment |  | Other
Agriculture Equipment
Other
Battery Storage
Biomass Combustion
CHP (Combined Heat & Power)
Cogeneration
Hydropower
Natural Gas
Solar Panel
Wind
None
| BuildingType |  | Type of AC/Heat Use:
| Assembly |  | Air Conditioning/Gas Heat
| Auto Repair |  | No Air Conditioning/Gas Heat
| Dormitory |  | Air Conditioning/Electric Heat
| Medical - Hospital |  | No Air Conditioning/Electric Heat
| Light Industrial |  | Heat Pump
| Lodging - Hotel |  | Constant Air Volume without economizer
| Lodging - Motel |  | Constant Air Volume with economizer
| Office - Small |  | Variable Air Volume without economizer
| Office - Large |  | Variable Air Volume with economizer
Other
Religious Worship
Restaurant - Fast Food
Restaurant - Full Service
Grocery
Retail - Small
Retail - Large
Retail - Big Box
Education - Primary School
Education - Secondary School
Education - Community College
Education - University
Warehouse
Note on C58: Can overwrite if incorrect. Please highlight if original selection was different from what was found.
Note on F58: Can overwrite if incorrect. Please highlight if original selection was different from what was found.
Note on H58: Can overwrite if incorrect. Please highlight if original selection was different from what was found.
Note on I58: Can overwrite if incorrect. Please highlight if original selection was different from what was found.

## Project Summary
FOR UTILITY USE ONLY
NAME / ADDRESS OF ACCOUNT: | 0
O&R Account Number: | 0
Project Number: | 0
Measure: | Prescriptive Electric HVAC Measures
SAVINGS SUMMARY
Gross
Peak Demand Savings | 0 | kW
Energy Savings | 0 | kWh
REBATE SUMMARY
Project Rebate | 0
PAYBACK SUMMARY
Material Cost | 0
Labor Cost | 0
TOTAL COST OF PROJECT
Incremental Cost (IMC) |  |  | Fill this out; to be autopopulated in a later iteration of the calculator.
Rate ($/kWh) | #DIV/0!
Simple Payback (Full Cost) | #VALUE! | yrs | Based on Full Measure Cost
Simple Payback w/ Rebate (Full Cost) | #VALUE! | yrs | Based on Full Measure Cost
Simple Payback (Inc. Cost) | #DIV/0! | yrs | Based on Incremental Measure Cost
Simple Payback w/ Rebate (Inc. Cost) | #DIV/0! | yrs | Based on Incremental Measure Cost
Annual Usage |  | kWh | Input Required
Annual Spend |  | $ | Input Required
Savings Percentage of Annual Usage | #DIV/0!

## ImportCSV
Measure # | Import? | quantity | Measure_Life | facility_type | building_type | MEASURE_CODE | cooling_type | Number_Units | Manufacturer | Model | Serial_number | Capacity | capacity_heating | HSPF | number_units_recommended | Tons | Efficiency | Temp_Heat | Temp_Cool | Tons_Controlled | heating_efficiency | Baseline_HSPF | basecase_seer | SEER | Baseline_EER | EER | Baseline_COP | COP | Full_Load_Hours_Heat | Full_Load_Hours_Cool | set_back_temp_heat | set_back_temp_cooling | existing_type | Equipment_Type | control_type | KWH_Cooling | kWh_heating | KWH_IMPACT | KW_IMPACT | LIFETIME_SAVINGS | kw_impact_1 | Installed_Cost | incentive_rate | ELEC_UTIL_CUST_INCENTIVE | GAS_UTIL_CUST_INCENTIVE | INCENTIVE_AMOUNT | NATURAL_GAS_SAVINGS_MMBTU | Total_MMBTU | Description | installer_id | _Qualifying_Measure | temperature_desc | supply_air_temp_reset | ELIGIBLE_COST | INDICATOR_1 | INDICATOR_2 | INDICATOR_3 | INDICATOR_4 | event_hrs | system_type | distribution | Activity | approved
| No | 1 |  | Commercial_Industrial | 0 | 0 |  | 0 | 0 | 0 | 0 | [30 empty] | 0 |  |  |  | 0 | 0 | 0
| No | 1 |  | Commercial_Industrial | 0 | 0 |  | 0 | 0 | 0 | 0 | [30 empty] | 0 |  |  |  | 0 | 0 | 0
| No | 1 |  | Commercial_Industrial | 0 | 0 |  | 0 | 0 | 0 | 0 | [30 empty] | 0 |  |  |  | 0 | 0 | 0
| No | 1 |  | Commercial_Industrial | 0 | 0 |  | 0 | 0 | 0 | 0 | [30 empty] | 0 |  |  |  | 0 | 0 | 0
| No | 1 |  | Commercial_Industrial | 0 | 0 |  | 0 | 0 | 0 | 0 | [30 empty] | 0 |  |  |  | 0 | 0 | 0
| No | 1 |  | Commercial_Industrial | 0 | 0 |  | 0 | 0 | 0 | 0 | [30 empty] | 0 |  |  |  | 0 | 0 | 0
| No | 1 |  | Commercial_Industrial | 0 | 0 |  | 0 | 0 | 0 | 0 | [30 empty] | 0 |  |  |  | 0 | 0 | 0
| No | 1 |  | Commercial_Industrial | 0 | 0 |  | 0 | 0 | 0 | 0 | [30 empty] | 0 |  |  |  | 0 | 0 | 0
| No | 1 |  | Commercial_Industrial | 0 | 0 |  | 0 | 0 | 0 | 0 | [30 empty] | 0 |  |  |  | 0 | 0 | 0
| No | 1 |  | Commercial_Industrial | 0 | 0 |  | 0 | 0 | 0 | 0 | [30 empty] | 0 |  |  |  | 0 | 0 | 0
| No | 1 |  | Commercial_Industrial | 0 | 0 |  | 0 | 0 | 0 | 0 | [30 empty] | 0 |  |  |  | 0 | 0 | 0
| No | 1 |  | Commercial_Industrial | 0 | 0 |  | 0 | 0 | 0 | 0 | [30 empty] | 0 |  |  |  | 0 | 0 | 0
| No | 1 |  | Commercial_Industrial | 0 | 0 |  | 0 | 0 | 0 | 0 | [30 empty] | 0 |  |  |  | 0 | 0 | 0
| No | 1 |  | Commercial_Industrial | 0 | 0 |  | 0 | 0 | 0 | 0 | [30 empty] | 0 |  |  |  | 0 | 0 | 0
| No | 1 |  | Commercial_Industrial | 0 | 0 |  | 0 | 0 | 0 | 0 | [30 empty] | 0 |  |  |  | 0 | 0 | 0
| No | 1 |  | Commercial_Industrial | 0 | 0 |  | 0 | 0 | 0 | 0 | [30 empty] | 0 |  |  |  | 0 | 0 | 0
| No | 1 |  | Commercial_Industrial | 0 | 0 |  | 0 | 0 | 0 | 0 | [30 empty] | 0 |  |  |  | 0 | 0 | 0
| No | 1 |  | Commercial_Industrial | 0 | 0 |  | 0 | 0 | 0 | 0 | [30 empty] | 0 |  |  |  | 0 | 0 | 0
| No | 1 |  | Commercial_Industrial | 0 | 0 |  | 0 | 0 | 0 | 0 | [30 empty] | 0 |  |  |  | 0 | 0 | 0
| No | 1 |  | Commercial_Industrial | 0 | 0 |  | 0 | 0 | 0 | 0 | [30 empty] | 0 |  |  |  | 0 | 0 | 0
| No | 1 |  | Commercial_Industrial | 0 | 0 |  | 0 | 0 | 0 | 0 | [30 empty] | 0 |  |  |  | 0 | 0 | 0
| No | 1 |  | Commercial_Industrial | 0 | 0 |  | 0 | 0 | 0 | 0 | [30 empty] | 0 |  |  |  | 0 | 0 | 0
| No | 1 |  | Commercial_Industrial | 0 | 0 |  | 0 | 0 | 0 | 0 | [30 empty] | 0 |  |  |  | 0 | 0 | 0
| No | 1 |  | Commercial_Industrial | 0 | 0 |  | 0 | 0 | 0 | 0 | [30 empty] | 0 |  |  |  | 0 | 0 | 0
| No | 1 |  | Commercial_Industrial | 0 | 0 |  | 0 | 0 | 0 | 0 | [30 empty] | 0 |  |  |  | 0 | 0 | 0
| No | 1 |  | Commercial_Industrial | 0 | 0 |  | 0 | 0 | 0 | 0 | [30 empty] | 0 |  |  |  | 0 | 0 | 0
| No | 1 |  | Commercial_Industrial | 0 | 0 |  | 0 | 0 | 0 | 0 | [30 empty] | 0 |  |  |  | 0 | 0 | 0
| No | 1 |  | Commercial_Industrial | 0 | 0 |  | 0 | 0 | 0 | 0 | [30 empty] | 0 |  |  |  | 0 | 0 | 0
| No | 1 |  | Commercial_Industrial | 0 | 0 |  | 0 | 0 | 0 | 0 | [30 empty] | 0 |  |  |  | 0 | 0 | 0
| No | 1 |  | Commercial_Industrial | 0 | 0 |  | 0 | 0 | 0 | 0 | [30 empty] | 0 |  |  |  | 0 | 0 | 0
| No | 1 |  | Commercial_Industrial | 0 | 0 |  | 0 | 0 | 0 | 0 | [30 empty] | 0 |  |  |  | 0 | 0 | 0
| No | 1 |  | Commercial_Industrial | 0 | 0 |  | 0 | 0 | 0 | 0 | [30 empty] | 0 |  |  |  | 0 | 0 | 0
Project Cost - HVAC | Yes | 1 | [46 empty] | Electric HVAC - 2021
Inspection - HVAC | No | 1 | [52 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## EFLH (hidden)
Type | Commercial_Industrial | EFLH_h | EFLH_c | AC/HP | Economizer ΔkWh/ton
Split System - S | Assembly | 603 | 669 | Air conditioner | 27 | Assembly¦Auto Repair¦Dormitory¦Medical - Hospital¦Light Industrial¦Lodging - Hotel¦Lodging - Motel
Single Package - P | Auto Repair | 1910 | 426 | Heat pump | 61
Split System - S or Single Package - P | Dormitory | 465 | 800 |  | 61
Central DX AC - D | Medical - Hospital | 3366 | 1424 |  | 61
Air Source Heat Pump (Split System) - AS | Light Industrial | 714 | 549 |  | 25
Air Source Heat Pump (Single Package) - AP | Lodging - Hotel | 1077 | 2918 |  | 61
Water Source Heat Pump - W | Lodging - Motel | 619 | 1233 |  | 61
Packaged Terminal AC - PTAC | Office - Small | 431 | 955 |  | 186
Packaged Terminal HP - PTHP | Office - Large | 2034 | 720 |  | 186
Single Packaged Vertical AC - PVAC | Other | 681 | 736 |  | 61
Single Packaged Vertical HP - PVHP | Religious Worship | 722 | 279 |  | 6
WC - Groundwater Source Heat Pump | Restaurant - Fast Food | 813 | 645 |  | 39
GC - Ground Source Heat Pump | Restaurant - Full Service | 821 | 574 |  | 31
| Grocery | 191 | 1279 |  | 61
| Retail - Small | 545 | 882 |  | 95
| Retail - Large | 2101 | 1068 |  | 95
| Retail - Big Box | 191 | 1279 |  | 152
| Education - Primary School | 840 | 394 |  | 42
| Education - Secondary School | 901 | 466 |  | 42
| Education - Community College | 1431 | 846 |  | 42
| Education - University | 1191 | 1208 |  | 42
| Warehouse | 452 | 400 |  | 2
| Low-Rise, Prior to 1979 | 757 | 507 |  | 61
| Low-Rise, From 1979 to 2006 | 723 | 550 |  | 61
| Low-Rise, From 2007 to Present | 503 | 562 |  | 61
*NOTE: This page is also used for the Ground Source Heat Pump tab | High-Rise, Prior to 1979 | 526 | 793 |  | 61
| High-Rise, From 1979 to 2006 | 395 | 843 |  | 61
| High-Rise, From 2007 to Present | 219 | 954 |  | 61

## List (hidden)
Measures |  | Reason |  | Building Type | Heating Type
Electric Chillers |  | New |  | Commercial_Industrial | Electric Furnace
Electric Unitary HVAC |  | Retrofit/Replaced |  | Multi-family | Heat Pump
Food Service Equipment |  |  |  |  | Gas Furnace
Ground Source Heat Pump
Refrigeration Controls
Refrigeration Doors
Refrigeration ECM Motors
Variable Frequency Drives
For HVAC Controls:
Equipment Type
AC with Electric Resistance Heat
AC with Gas Heat
Air-Source Heat Pump
Other Cooling with Electric Heat
Vintage
New
Existing
Existing Control Type | Cool% | Electric Heat% | Gas% | Smart Thermostat savings, MidAtlantic TRM v10
Manual | 0.05 | 0.04 | 0.05
Programmable | 0.03 | 0.02 | 0.02
Unknown | 0.03 | 0.02 | 0.02
1 | 64999 | < 5.4 tons
65000 | 134999 | >= 5.4 to <11.25 tons
135000 | 239999 | >= 11.25 to < 20 tons
240000 | 759999 | >= 20 to < 63 tons
760000 | 999999999 | > 63 tons
135000 | >= 11.25 to < 20 tons
Efficiency Lookup | Cooling Efficiency | Heating Efficiency COP/HSPF | Code
NewAC with Electric Resistance Heat< 5.4 tons | 13 | 1 | ASHRAE 90.1-2016
NewAC with Electric Resistance Heat>= 5.4 to <11.25 tons | 11.2 | 1 | ASHRAE 90.1-2016
NewAC with Electric Resistance Heat>= 11.25 to < 20 tons | 11 | 1 | ASHRAE 90.1-2016
NewAC with Electric Resistance Heat>= 20 to < 63 tons | 10 | 1 | ASHRAE 90.1-2016
NewAC with Electric Resistance Heat> 63 tons | 9.7 | 1 | ASHRAE 90.1-2016
NewAC with Gas Heat< 5.4 tons | 13 | na | ASHRAE 90.1-2016
NewAC with Gas Heat>= 5.4 to <11.25 tons | 11 | na | ASHRAE 90.1-2016
NewAC with Gas Heat>= 11.25 to < 20 tons | 10.8 | na | ASHRAE 90.1-2016
NewAC with Gas Heat>= 20 to < 63 tons | 9.8 | na | ASHRAE 90.1-2016
NewAC with Gas Heat> 63 tons | 9.5 | na | ASHRAE 90.1-2016
NewAir-Source Heat Pump< 5.4 tons | 14 | 8.2 | ASHRAE 90.1-2016
NewAir-Source Heat Pump>= 5.4 to <11.25 tons | 11 | 3.3 | ASHRAE 90.1-2016
NewAir-Source Heat Pump>= 11.25 to < 20 tons | 10.6 | 3.2 | ASHRAE 90.1-2016
NewAir-Source Heat Pump>= 20 to < 63 tons | 9.5 | 3.2 | ASHRAE 90.1-2016
NewAir-Source Heat Pump> 63 tons | 9.5 | 3.2 | ASHRAE 90.1-2016
ExistingAC with Electric Resistance Heat< 5.4 tons | 13 | 1 | ASHRAE 90.1-2013
ExistingAC with Electric Resistance Heat>= 5.4 to <11.25 tons | 11.2 | 1 | ASHRAE 90.1-2013
ExistingAC with Electric Resistance Heat>= 11.25 to < 20 tons | 11 | 1 | ASHRAE 90.1-2013
ExistingAC with Electric Resistance Heat>= 20 to < 63 tons | 10 | 1 | ASHRAE 90.1-2013
ExistingAC with Electric Resistance Heat> 63 tons | 9.7 | 1 | ASHRAE 90.1-2013
ExistingAC with Gas Heat< 5.4 tons | 13 | na | ASHRAE 90.1-2013
ExistingAC with Gas Heat>= 5.4 to <11.25 tons | 11 | na | ASHRAE 90.1-2013
ExistingAC with Gas Heat>= 11.25 to < 20 tons | 10.8 | na | ASHRAE 90.1-2013
ExistingAC with Gas Heat>= 20 to < 63 tons | 9.8 | na | ASHRAE 90.1-2013
ExistingAC with Gas Heat> 63 tons | 9.5 | na | ASHRAE 90.1-2013
ExistingAir-Source Heat Pump< 5.4 tons | 13 | 7.7 | ASHRAE 90.1-2013
ExistingAir-Source Heat Pump>= 5.4 to <11.25 tons | 11 | 3.3 | ASHRAE 90.1-2013
ExistingAir-Source Heat Pump>= 11.25 to < 20 tons | 10.6 | 3.2 | ASHRAE 90.1-2013
ExistingAir-Source Heat Pump>= 20 to < 63 tons | 9.5 | 3.2 | ASHRAE 90.1-2013
ExistingAir-Source Heat Pump> 63 tons | 9.5 | 3.2 | ASHRAE 90.1-2013
***Using EER instead of EER, per NJCEP Protocols FY20/21

## Version (hidden)
Version | Date | Note
1 | 2021-06-28 | Workbook drafted
2 | 2021-11-04 | Qced and Finalized
3 | 2022-01-10 | Project Summary Form added
4 | 2022-01-28 | Inspection form added, smart thermostat added
5 | 2022-01-31 | Added several fields - heating capacity, other identifiers; changed kWh savings calculation to be based on SEER/EER rather than SEER/IEER.
| 2022-02-07 | Adjusted based on EMV group and FY2020 order from Jan/Feb 2022: - Reduced baselines to SEER 13 for <5.4 ton AC - Change baseline IEER for 5.4-11.25 ton ASHP to 11 - Change qualifying EER for DHP to 13 instead of 14
| 2022-02-15 | Finalization
6 | 2022-04-06 | Changing kWh savings calculations back to SEER/IEER instead of SEER/EER based on latest EM&V Group guidance